## Problem 1
| Reported conc. | MCL
Turbidity | 170 NTU | ~0 | Too high
Iron | 13.0 mg/L | 0.3 | Too high
Manganese | 1.0 mg/L | 0.05 | Too high
Taste & odor | Unacceptable in summer |  | Too high
|  | Conc | MW | Equiv | Eq Wt | Equiv conc | Conc | Sum Eq
|  | mg/L |  |  |  | meq/L | mg/L as CaCO3 | meq/L
Calcium | 50.8 mg/L | 50.8 | 40 | 2 | 20 | 2.54 | 127
Magnesium | 0.9 mg/L | 0.9 | 24.4 | 2 | 12.2 | 0.07377 | 3.6885
Sodium | 6.9 mg/L | 6.9 | 23 | 1 | 23 | 0.3 | 15
Potassium | 0.4 mg/L | 0.4 | 39.1 | 1 | 39.1 | 0.01023 | 0.51151 | 2.924
Carbonate | 0 mg/L | 0 | 60 | 2 | 30 | 0 | 0
Bicarbonate | 116 mg/L | 116 | 61 | 1 | 61 | 1.9016 | 95.082
Sulfate | 31.0 mg/L | 31 | 96 | 2 | 48 | 0.64583 | 32.2917
Chloride | 10.8 mg/L | 10.8 | 35.5 | 1 | 35.5 | 0.30423 | 15.2113
Nitrate | 1.9 mg/L as NO3 | 1.9 | 62 | 1 | 62 | 0.030645 | 1.5323 | 2.8823
Hardness | [6 empty] | 130.6885 | OK
Alkalinity | [6 empty] | 95.082
Treatment technologies:
| Turbidity | Sedimentation with coagulant addition, followed by rapid filtration
| Iron and manganese | Oxidation, probably by permanganate since Mn is high
| Taste and odor | Oxidation may treat t&o, otherwise activated carbon or perhaps ozonation
| Disinfection (always) | Ozonation - may help with taste and odor. Also need combined chlorine for residual
| Fluoridation (always) | Flouride addition

## Problem 2
| Reported conc. | MCL
Turbidity | 0.1 NTU | ~0 | OK
Iron | 0.2 mg/L | 0.3 | OK
Manganese | 0.04 mg/L | 0.05 | OK
Chloride | 210 mg/L | 250 | Marginal
Sulfate | 240 mg/L | 250 | Marginal
Sodium | 117 mg/L | 20 | Guidance level only, but potentially a problem
|  | Conc | MW | Equiv | Eq Wt | Equiv conc | Conc | Sum Eq
|  | mg/L |  |  |  | meq/L | mg/L as CaCO3 | meq/L
Calcium | 121 mg/L | 121 | 40 | 2 | 20 | 6.05 | 302.5
Magnesium | 57 mg/L | 57 | 24.4 | 2 | 12.2 | 4.6721 | 233.6066
Sodium | 117 mg/L | 117 | 23 | 1 | 23 | 5.087 | 254.3478
Potassium | 3 mg/L | 3 | 39.1 | 1 | 39.1 | 0.076726 | 3.8363 | 15.8858
Carbonate | 0 mg/L | 0 | 60 | 2 | 30 | 0 | 0
Bicarbonate | 298 mg/L | 298 | 61 | 1 | 61 | 4.8852 | 244.2623
Sulfate | 240 mg/L | 240 | 96 | 2 | 48 | 5 | 250
Chloride | 210 mg/L | 210 | 35.5 | 1 | 35.5 | 5.9155 | 295.7746
Nitrate | 7.4 mg/L as NO3 | 7.4 | 62 | 1 | 62 | 0.11935 | 5.9677 | 15.9201
Hardness | [6 empty] | 536.1066 | Too high
Alkalinity | [6 empty] | 244.2623
Treatment technologies:
| Hardness | Lime and soda ash needed to remove carbonate and non-carbonate hardness
| Disinfection (always) | Ozonation or chlorination. Also need combined chlorine for residual
| Fluoridation (always) | Flouride addition